- Specifications

| Nominal Voltage | 12V |
| --- | --- |
| Rated Capacity 770F(250C) (10HR) | 65.0Ah |
| Dimensions (mm) | Length | 350±3 |
|  | Width | 167±2 |
|  | Height | 181±2 |
|  | Total Height | 183±2 |
| Approx. Weight (kg) | 20 |
| Terminal | T12 |

- Characteristic

| Capacity 770F(250C) | 20HR (3.445A) | 69.0Ah |
| --- | --- | --- |
|  | 10HR (6.500A) | 65.0Ah |
|  | 5HR (11.05A) | 55.3Ah |
|  | 1HR (35.75A) | 35.8Ah |
|  | 15 min rate (113.8A) | 28.4Ah |
| Internal Resistance | Full Charged Battery 770F(250C) | Approx. 6mΩ |
| Temperature dependence of capacity (10HR) | 1040F(400C) | 102% |
|  | 770F(250C) | 100% |
|  | 320F(00C) | 85% |
|  | 50F(-150C) | 65% |
| Self-Discharge 680F(200C) (Capacity after) | 3 months | 90% |
|  | 6 months | 80% |
|  | 12 months | 60% |
| Max. Discharge Current, 770F(250C) | 520A(5s) |
| Floating design life, 770F(250C) | 10 years |
| Constant Voltage Charge,770F(250C) | Cycle | 14.4~14.7V(-24mV/0C) max. current: 16.25 A |
|  | Float | 13.6~13.8V(-18mV/0C) |

| Constant Current Discharge Characteristics (A), 770F(250C) |
| --- |
| F.V/TIME | 5min | 10min | 15min | 30min | 60min | 2H | 3H | 5H | 8H | 10H | 20H |
| 1.60V/cell | 221.0 | 143.0 | 113.8 | 65.0 | 37.7 | 23.42 | 17.26 | 11.67 | 7.80 | 6.78 | 3.54 |
| 1.70V/cell | 210.0 | 135.9 | 108.6 | 62.1 | 36.4 | 22.52 | 16.87 | 11.45 | 7.72 | 6.71 | 3.51 |
| 1.75V/cell | 200.2 | 127.4 | 106.7 | 60.8 | 35.8 | 22.10 | 16.54 | 11.25 | 7.56 | 6.60 | 3.48 |
| 1.80V/cell | 187.9 | 117.7 | 104.8 | 59.7 | 35.2 | 21.72 | 16.25 | 11.05 | 7.48 | 6.50 | 3.45 |
| Constant Wattage Discharge Characteristics (Watt), 770F(250C) |
| F.V/TIME | 5min | 10min | 15min | 30min | 60min | 2H | 3H | 5H | 8H | 10H | 20H |
| 1.60V/cell | 392.3 | 259.8 | 208.5 | 119.7 | 69.8 | 43.72 | 32.51 | 22.17 | 14.95 | 13.22 | 6.92 |
| 1.70V/cell | 376.2 | 249.1 | 200.9 | 115.5 | 67.9 | 42.42 | 32.05 | 21.95 | 14.93 | 13.20 | 6.91 |
| 1.75V/cell | 362.1 | 235.7 | 199.1 | 114.1 | 67.3 | 41.99 | 31.69 | 21.74 | 14.76 | 13.08 | 6.90 |
| 1.80V/cell | 342.8 | 219.6 | 197.3 | 112.9 | 66.8 | 41.63 | 31.41 | 21.55 | 14.70 | 13.00 | 6.89 |