- Specifications

| Nominal Voltage | 12V |
| --- | --- |
| Rated Capacity 770F(250C) (10HR) | 70.0Ah |
| Dimensions (mm) | Length | 259±3 |
|  | Width | 168±2 |
|  | Height | 211±3 |
|  | Total Height | 214±3 |
| Approx. Weight (kg) | 20.5 |
| Terminal | T12 |

- Characteristic

| Capacity 770F(250C) | 20HR (3.71A) | 74.2Ah |
| --- | --- | --- |
|  | 10HR (7.00A) | 70.0Ah |
|  | 5HR (11.9A) | 59.5Ah |
|  | 1HR (38.5A) | 38.5Ah |
|  | 15 min rate (122.5A) | 30.6Ah |
| Internal Resistance | Full Charged Battery 770F(250C) | Approx. 5.5mΩ |
| Temperature dependence of capacity (10HR) | 1040F(400C) | 102% |
|  | 770F(250C) | 100% |
|  | 320F(00C) | 85% |
|  | 50F(-150C) | 65% |
| Self-Discharge 680F(200C) (Capacity after) | 3 months | 90% |
|  | 6 months | 80% |
|  | 12 months | 60% |
| Max. Discharge Current, 770F(250C) | 560A(5s) |
| Floating design life, 770F(250C) | 10 years |
| Constant Voltage Charge,770F(250C) | Cycle | 14.4~14.7V(-24mV/0C) max. current: 17.5 A |
|  | Float | 13.6~13.8V(-18mV/0C) |

| Constant Current Discharge Characteristics (A), 770F(250C) |
| --- |
| F.V/TIME | 5min | 10min | 15min | 30min | 60min | 2H | 3H | 5H | 8H | 10H | 20H |
| 1.60V/cell | 238.0 | 154.0 | 122.5 | 70.0 | 40.7 | 25.22 | 18.59 | 12.57 | 8.40 | 7.30 | 3.81 |
| 1.70V/cell | 226.1 | 146.3 | 117.0 | 66.9 | 39.2 | 24.26 | 18.17 | 12.33 | 8.31 | 7.23 | 3.78 |
| 1.75V/cell | 215.6 | 137.2 | 114.9 | 65.5 | 38.5 | 23.80 | 17.81 | 12.11 | 8.14 | 7.11 | 3.75 |
| 1.80V/cell | 202.3 | 126.7 | 112.8 | 64.3 | 37.9 | 23.39 | 17.50 | 11.90 | 8.05 | 7.00 | 3.71 |
| Constant Wattage Discharge Characteristics (Watt), 770F(250C) |
| F.V/TIME | 5min | 10min | 15min | 30min | 60min | 2H | 3H | 5H | 8H | 10H | 20H |
| 1.60V/cell | 422.4 | 279.8 | 224.5 | 128.9 | 75.3 | 47.08 | 35.01 | 23.88 | 16.10 | 14.24 | 7.45 |
| 1.70V/cell | 405.1 | 268.2 | 216.4 | 124.4 | 73.2 | 45.68 | 34.52 | 23.64 | 16.08 | 14.22 | 7.44 |
| 1.75V/cell | 389.9 | 253.8 | 214.4 | 122.9 | 72.5 | 45.22 | 34.13 | 23.41 | 15.88 | 14.09 | 7.43 |
| 1.80V/cell | 369.2 | 236.5 | 212.5 | 121.6 | 72.0 | 44.83 | 33.73 | 23.21 | 15.83 | 14.00 | 7.42 |